BARD MANUFACTURING COMPANY, INC.

Q24A2-Q60A2 Series Air Conditioner

Engineering Specification Guide

1.0	GENERAL

Furnish and install a self-contained, vertical, floor standing, through-	the-wall air conditioner be manufactured by Bard Manufacturing Company, Inc.  The unit shall be approved and listed by Intertek ETL Listed (ETL US/C) to ANSI/UL 1995/CSA22.2 No. 236-05, latest edition.  Unit shall be factory assembled, pre-charged, pre-wired, tested and ready to operate.  Unit performance shall be certified in accordance with the Air Conditioning Heating and Refrigeration Institute Standard 390-2003 for Single Package Vertical Units.

Unit shall include 5 year parts warranty covering compressor, parts, and heat exchange coils, subject to terms and conditions of Bard Limited Warranty agreement.

Unit efficiency shall be specified in terms of EER.

Manufacturers: Capacities shall be as indicated on drawings and units shall be manufactured by Bard Manufacturing Company, Inc. or prior approved equal.

2.0	CONSTRUCTION FEATURES

2.1	CABINET

Constructed of 20 gauge pre-painted or vinyl laminated galvanized steel.  Choices available are either two-tone (vinyl) finish with “slate” front panels and “platinum” cabinet for designer appearance,  (gray) or (beige) painted steel (select one).  Vinyl finish is very resistant to scratching and marring and is easy to clean.  Tamper resistant fasteners are provided for access panels.  Unit includes built-in rollers for each installation into wall sleeve and removal for service, if necessary.  Front panel is hinged and lockable for filter service and access to primary functional electrical controls.

2.2	INSULATION

Cabinet is fully insulated with foil covered, high density fiberglass insulation with sealed edge treatment and special sound deadening insulation material in the compressor section.  All insulation is designed to resist mold and mildew growth and facilitate ease of cleaning.

2.3	COMPRESSOR

All models shall use a high efficiency scroll compressor for maximum efficiency and reliability.  The compressor shall be covered by a 5-year parts warranty.  The refrigeration circuit shall be equipped with factory installed high and low pressure controls, liquid line filter dryer, and discharge muffler.  The scroll compressor does not require a crankcase heater or accumulator.  The refrigeration control shall be a factory installed TXV. Refrigeration service ports shall be included and located with easy access.  Refrigerant shall be R-410A.  Compressor shall have double isolated floating mounting system and compressor sound blanket.

2.4	CONDENSATE DRAIN SYSTEM

Condensate shall be removed from the unit by connections located in the back or side of the unit.  The evaporator and condenser coils shall have separate drain pans constructed of stainless steel to eliminate corrosion.  The lower unit base serves as a secondary drain pan.

2.5	CONDENSER FAN MOTOR

The condenser fan motor shall be a permanent split capacitor, outdoor motor with double oil capacity sleeve bearings and totally enclosed.

2.6	INDOOR BLOWER MOTOR

The indoor blower motor shall be a variable speed (ECM) type to produce the same rated air flow from 0 to .8 inch WC of external static pressure (.5 on Q24H model) at low sound levels.  The motor is to be self adjusting to provide proper rated air flow at high static pressures without user adjustment or wiring changes by the user.  The motor shall be programmed for 20-second ramp up and 60-second down rate for quiet, smooth starting and stopping. PSC motor shall not be acceptable.

2.7	ELECTRICAL COMPONENTS

Electrical components are easily accessible for routine inspection and maintenance through front service panels.  Circuit breaker is standard on all 208/230 volt models and rotary disconnect standard on all 460 volt models.  Circuit breaker/rotary disconnect access is through lockable access panel.  Lock and key are provided as standard equipment.  Unit shall have single point entry for line voltage.

2.8	CONTROL CIRCUIT

The internal control circuit shall consist of a current limiting 24VAC type 50VA transformer. To prevent rapid compressor short cycling, a five-minute time delay circuit shall be factory installed.  A low pressure bypass shall be factory installed to prevent nuisance tripping during low temperature start-up.

All units with 3-phase power shall include factory mounted phase rotation monitor. This device shall protect scroll compressor from reverse rotation and also protect unit from phase failure. If 3-phase power is incorrectly connected at the field power connections, the phase monitor shall lock out the unit and a red light will illuminate indicating incorrect phase. Also if a power leg is lost, the phase monitor will lockout the unit due to phase imbalance. Once the condition is corrected, turning the power off at the circuit breaker or disconnect will reset the phase monitor.

2.9	SERVICE FEATURES

The unit shall include a diagnostic light to indicate when service is required.  System Service shall detect high or low pressure control operation.

3.0	HEAT OPTIONS (Select One)

3.1	None

3.2	Electric Heat

The air conditioner shall have a factory installed electric resistance heater available that is designed specifically for application in the Q-Tec Series air conditioner.  Heater shall include automatic limit safety controls.

3.3	 HOT WATER COIL

The hot water coil shall be factory mounted in discharge air plenum, or for ducted application, coil is complete with 3-way valve and can be wired for first or second stage heat.

4.0	VENTILATION OPTIONS (Select One)

Q-Tec models are designed to provide optional ventilation packages to meet all of your ventilation and indoor air quality requirements.  All ventilation packages are factory installed.

4.1	BAROMETRIC FRESH AIR DAMPER		      STANDARD

The barometric fresh air damper is a standard feature on all models.  It allows outside ventilation air, up to 25% of the total air flow rating of the unit, to be introduced through the air inlet openings and to be mixed with the conditioned air.  The damper opens during blower operation and closes when the blower is off.  Adjustable blade stops allow different amounts of outside air to be introduced into the building and can be easily locked closed if required.

4.2	BLANK OFF PLATE					       OPTIONAL

A blank off plate covers the air inlet openings which restrict any outside air from entering the unit.  The blank off plate should be utilized in applications where outside air is not required to be mixed with the conditioned air.

4.3	COMMERCIAL ROOM VENTILATOR		        OPTIONAL

The built-in commercial room ventilator is internally mounted and allows outside ventilation air, up to 50% of the total air flow rating of the unit, to be introduced through the air inlet openings.  It includes a built-in exhaust air damper.  The commercial room ventilator (CRV) shall be easily removed for maintenance or replacement.  The damper can be easily adjustable, to control the amount of fresh air supplied into the unit.  The CRV can be controlled by indoor blower operation or field controlled based on room occupancy or schedule.  Unit complies with ANSI/ASHRAE Standard 62.1 Ventilation for Acceptable Air Quality.

Two Models Available (select 1):	Spring Return on Power Loss or Deactivation - Vent Option V

Power Return (will not close on power loss) –  Vent Option P

4.4	ENERGY RECOVERY VENTILATOR		       OPTIONAL

The Energy Recovery Ventilator (ERV) shall consist of 1 or 2 rotary wheels in an insulated cassette frame with seals, drive motor and belt. The ERV assembly shall also include intake and exhaust blowers. The entire assembly shall easily slide in or out of the ventilation section, allowing for maintenance or replacement. The total energy wheel shall be coated with silica gel desiccant, permanently bonded without the use of binders or adhesives. The coated segments shall be washable with detergent or alkaline coil cleaner and water. Desiccant shall not dissolve or deliquesce in the presence of water or high humidity.  All diameter and perimeter seals shall be provided as part of the cassette assembly and shall be factory set. Drive belts shall not require external tensioners or adjustment. Cassette wheels shall include rims to prevent belts from slipping off wheels.   Intake and exhaust blowers shall have selections of high, medium or low speed and selected independently, to allow for positive pressurization if desired. The ERV cassette including parts and media shall  include 5year warranty subject to terms and conditions of Bard’s warranty.

The ERV thermal performance shall be certified by the manufacturer in accordance with ASHRAE Standard 84, Method of Testing Air-to Air Heat Exchangers and ARI  Standard 1060, Rating for Air-to-Air Energy Recovery Ventilation Equipment Cassettes, and shall be listed in the ARI Certified Products. Unit complies with ANSI/ASHRAE Standard 62.1 Ventilation for Acceptable Air Quality.

5.0	FILTER OPTIONS  - (Select One)

5.1	1” Fiberglass

5.2	2” Fiberglass – Pleated – MERV 6

6.0	HOT GAS REHEAT (OPTIONAL, Factory Installed)

6.1	The dehumidification circuit incorporates an independent heat exchanger coil in the supply air stream in addition to the standard evaporator coil.  This coil reheats the supply air after it passes over the cooling coil, and is sized to nominally match the sensible cooling capacity of the evaporator coil.  Extended run times in dehumidification mode can be achieved using waste heat from the refrigeration cycle to achieve the reheat process, while at the same time large amounts of moisture can be extracted from the passing air stream.  Models that also have electric heaters installed have the electric heat inhibited during dehumidification mode, although it remains available for additional reheat during certain conditions. The dehumidification cycle shall be energized by a rise in relative humidity above set point. The unit shall energize in the cooling mode and also a two position valve will energize, allowing hot refrigerant gas to pass thru the reheat coil, reheating the cold air leaving the evaporator coil. The dehumidification cycle shall have on/off capability. If the thermostat calls for cooling or heating during the dehumidification cycle, the unit shall drop out of dehumidification to satisfy the call from the thermostat.  A solid state circuit board shall control the dehumidification function. The dehumidification option shall be factory installed.

7.0	CABINET COLOR – (Select One)

7.1	Washable Vinyl  -  Two-Tone Finish: Slate front with Platinum sides

7.2	Slate Gray

7.3     Beige

8.0	COIL OPTIONS – (Select Standard hydrophilic-coated evaporator and non-coated condenser coil or

Coated: Evaporator or Condenser Coils, or Both)

8.1	PHENOLIC COATING (TechniCoat)

Phenolic coating is a proprietary epoxy-modified phenolic dip coating.  It is the only anti-corrosive coating ever designed and custom engineered specifically for HVAC/R coils.  After years of research and 25 years of experience gained in coating almost 1,000,000 coils, TechniCoat is state of the art in corrosion control.  Total immersion ensures complete coverage with no significant loss of thermal efficiency.  The 4-step coating system consists of (1) a multi-step cleaning process, (2) chemical etch primer, (3) epoxy-modified phenolic, and (4) phenolic sealer.

9.0	CONTROLS – (Select one of the following factory mounted control options)

9.1	None

9.2	Electronic non-programmable

9.3	Electronic programmable

Thermostat shall have option for humidity control

Optional field installed CO2 sensor for ventilation control

10.0	ACCESSORIES

10.1	WALL SLEEVE (wall sleeve and louver required)

Wall sleeve shall be factory supplied and must be constructed of 16 gauge galvanized steel, coated with an epoxy primer and baked-on polyester enamel paint.  It shall be designed to withstand a minimum of 1000 hours of salt spray protection when tested per ASTM B117-03 standard.  One sleeve size fits models Q24A through Q42A.  Another size is required for Q48A and Q60A.

10.2	SIDE TRIM KITS

A standard side trim kit that will cover up to 4” space between the 
 		back of the unit and the wall is included with each unit.  Optional 10”, 
 		13” and 16” trim kits are available.

10.3	Furnish factory louver designed for condenser air and outside air intake and exhaust.  Louver shall be aluminum construction with removable core for service.  Access to removable core is by tamper-proof screws. Louver shall have a powder coat finish.  See our color chart for color selections.

10.4	AIR DISTRIBUTION – (Select 1)

10.4.1	The Q-Tec shall have a discharge air plenum with a double deflection register on the front.

10.4.2	The Q-Tec shall have a discharge air plenum with double deflection supply register on the front and both sides.

10.4.3  	The Q-Tec shall be ducted with a cabinet extension to cover ductwork

10.5  CONDENSATE DRAIN – (Select One)

10.5.1	Q-Tec unit shall have rear condensate system with factory trap.

10.5.2	Q-Tec unit shall have a heated rear condensate system with factory trap

11.0	WARRANTY

11.1	The Bard product specified shall be free from defects in materials and workmanship for a period of 5 years for compressor, and for a period of 5 years for all parts. Warranty period shall start from date of installation as stated on warranty card; or from date of shipment if no warranty card is returned to Bard Manufacturing.  Equipment must be used under normal conditions and warranty is subject to Bard Manufacturing’s standard limited warranty statement.

12.0	INSTALLATION

12.1	Installation shall be done in strict adherence to Bard’s Installation Instructions.